## COVER
CONSORTIUM OF
SINOPEC PETROLEUM ENGINEERING CORPORATION.
AND
ZICOM EQUIPMENT PTE. LTD.
BANGLADESH PETROLEUM EXPLORATION & PRODUCTION CO. LTD.
[6 empty] | 29 Tuas Avenue 3 Singapore 639420 |  |  |  | Tel | : +65 6865 1765
[6 empty] | E-mail | : zepl@zicomgroup.com |  |  | Fax | : +65 6865 1764
ELECTRICAL CALCULATION SHEET
[8 empty] | Doc. No: | 240-0214-EMEL-CS00-0001
|  | Job No. |  | : | 240
|  | Client |  | : | BANGLADESH PETROLEUM EXPLORATION & PRODUCTION CO. LTD.
|  | Location |  | : | SRIKAIL GAS FIELD, BANGLADESH
|  | Item No. |  | : | -
|  | Description |  | : | GENERATOR SIZING
|  | Project Title. |  | : | 60 MMSCFD GLYCOL DEHYDRATION TYPE GAS PROCESS PLANT
|  | Year Built |  | : | 2015
A | 2015-05-12 |  | 2 | ISSUED FOR APPROVAL | [5 empty] | AS | MH | VG
Rev. | Date |  | Page | Description of Revision | [5 empty] | Prepared | Checked | Approved
ZICOM

## Generator Size Calculation
GENERATOR SIZING
USER |  | BANGLADESH PETROLEUM EXPLORATION & PRODUCTION CO. LTD. |  |  |  | DOC NO. | 240-0214-EMEL-CS00-0001 |  | REV : A
LOCATION |  | SRIKAIL GAS FIELD, BANGLADESH |  |  |  | SERVICE
PROJECT |  | 60 MMSCFD GLYCOL DEHYDRATION TYPE GAS PROCESS PLANT |  |  |  | TAG NO. | N/A
JOB NO. |  | 240 |  |  |  | QUANTITY | N/A
No. | EQUIP. TAG NO. | EQUIPMENT |  | VOLTAGE RATING | DESCRIPTION | QTY | CONNECTED LOAD | OPERATING LOAD | REMARKS
BUS BAR GROUP A
1 | P-100A | CONDENSATE TRANSFER PUMP |  | 400 |  | 1 | 5500 | 5500
2 | P-100B |  |  | 400 |  | 1
3 | P-200A | COOLING TOWER PUMP |  | 400 |  | 1 | 5500 | 5500
4 | P-200B |  |  | 400 |  | 1
5 | E-100(1) | DRY AIR COOLER(1) |  | 400 |  | 1 | 22000 | 15000
6 | E-100(2) | DRY AIR COOLER(2) |  | 400 |  | 1 | 22000 | 15000
7 | E-100(3) | DRY AIR COOLER(3) |  | 400 |  | 1 | 15000 | 15000
8 | E-100(4) | DRY AIR COOLER(4) |  | 400 |  | 1 | 15000 | 15000
9 | E-300A(1) | REGENERATION GAS COOLER(A) |  | 400 |  | 1 | 22000 | 15000
10 | E-300A(2) |  |  | 400 |  | 1 | 15000 | 15000
11 | E-300B(1) | REGENERATION GAS COOLER(B) |  | 400 |  | 1 | 22000
12 | E-300B(2) |  |  | 400 |  | 1 | 15000
13 | E-400A(1) | COOLING GAS COOLER(A) |  | 400 |  | 1 | 22000 | 15000
14 | E-400A(2) |  |  | 400 |  | 1 | 15000 | 15000
15 | E-400B(1) | COOLING GAS COOLER(B) |  | 400 |  | 1 | 22000
16 | E-400B(2) |  |  | 400 |  | 1 | 15000
17 | P-800 | KNOCK OUT DRUM PUMP |  | 400 |  | 1 | 3000 | 3000
18 | CT-100 | WET COOLER |  | 400 |  | 1 | 11000 | 11000
19 | V-502A/B | AIR DRYER |  | 230 |  | 1 | 1000 | 1000
20 | V-503A/B | AIR DRYER |  | 230 |  | 1
21 | LCP-0801 | FLARE STACK LOCAL CONTROL PANEL |  | 230 |  | 1 | 3000 | 3000
22 | H-100 | WATER BATH HEATER |  | 400 |  | 1 | 6000 | 6000
23 | R-200 | REGENERATION GAS HEATER |  | 400 |  | 1 | 6000 | 6000
24 | P-403 | DEEP WELL PUMP |  | 400 |  | 1 | 11000 | 11000
25 | P-404 | POTABLE WATER PUMP |  | 400 |  | 1 | 750 | 750
26 | P-401A/B | JOCKEY PUMP CONTROL PANEL |  | 400 |  | 1 | 12000 | 12000
27 | P-402A | DIESEL FIRE WATER PUMP CONTROL PANEL |  | 400 |  | 1 | 3000 | 500
28 | P-402B | DIESEL FIRE WATER PUMP CONTROL PANEL |  | 400 |  | 1
29 | P-300A | RECYCLE PUMP |  | 400 |  | 1 | 750 | 750
30 | P-300B | RECYCLE PUMP |  | 400 |  | 1
31 | P-301A | TREATED WATER TRANSFER PUMP |  | 400 |  | 1 | 750 | 750
32 | P-301B | TREATED WATER TRANSFER PUMP |  | 400 |  | 1
33 | LDP-1401 | LIGHTING DISTRIBUTION PANEL |  | 400 |  | 1 | 18000 | 10000
34 | C-501 | UTILITY AIR COMPRESSOR |  | 400 |  | 1 | 15000 | 15000
35 | C-502 |  |  | 400 |  | 1
36 | C-503 |  |  | 400 |  | 1
37 | UPS-1 | UPS SYSTEM 1 |  | 230 |  | 1 | 4800 | 4800
38 | UPS-2 | UPS SYSTEM 1 |  | 230 |  | 1
39 | UPS-3 | UPS FIRE & GAS |  | 230 |  | 1 | 800 | 100
BUS BAR GROUP B
40 |  | DOMESTIC & OFFICE USES |  | 400 |  |  | 50000 | 50000
41 |  | GENERATOR & MCC ROOM |  | 400 |  |  | 10000 | 10000
[7 empty] | Total: | 276650
276.65
|  |  | Total Plant Load in Kw= | 276.65
|  |  | Base load =80% of Plant Load= | 221.32
|  |  | Calculated Generator= | 250
|  |  | Next available selected Generator Size= | 276
A | 2015-05-12 |  | ISSUED FOR APPROVAL |  |  | AS |  | MH | VG
REV | DATE |  | DESCRIPTION |  |  | PREPARED |  | CHECKED | APPROVED
ZICOM
CONSORTIUM OF
SINOPEC PETROLEUM ENGINEERING CORPORATION
AND
ZICOM EQUIPMENT PTE. LTD.
BANGLADESH PETROLEUM EXPLORATION & PRODUCTION CO. LTD.