## COVER
CONSORTIUM OF
SINOPEC PETROLEUM ENGINEERING CORPORATION.
AND
ZICOM EQUIPMENT PTE. LTD.
BANGLADESH PETROLEUM EXPLORATION & PRODUCTION CO. LTD.
[6 empty] | 29 Tuas Avenue 3 Singapore 639420 |  |  |  | Tel | : +65 6865 1765
[6 empty] | E-mail | : zepl@zicomgroup.com |  |  | Fax | : +65 6865 1764
ELECTRICAL DATA SHEET
[8 empty] | Doc. No: | 240-0301-EMEL-DS00-0002
|  | Job No. |  | : | 240
|  | Client |  | : | BANGLADESH PETROLEUM EXPLORATION & PRODUCTION CO. LTD.
|  | Location |  | : | SRIKAIL GAS FIELD, BANGLADESH
|  | Item No. |  | : | -
|  | Description |  | : | LOCAL CONTROL STATION
|  | Project Title. |  | : | 60 MMSCFD GLYCOL DEHYDRATION TYPE GAS PROCESS PLANT
A | 2015-05-12 |  | 3 | ISSUED FOR APPROVAL | [5 empty] | AS | MH | VG
Rev. | Date |  | Page | Description of Revision | [5 empty] | Prepared | Checked | Approved
ZICOM

## LCS with Selector Sw.
ELECTRICAL
DATA SHEET
USER | BANGLADESH PETROLEUM E&P CO. LTD. |  |  |  | DOC NO | 240-0301-EMEL-DS00-0002
LOCATION | SRIKAIL GAS FIELD,BANGLADESH |  |  |  | NAME | Local Control Station
PROJECT | 60 MMSCFD SILICAGEL DEHYDRATION TYPE GAS PROCESS PLANT |  |  |  | Version | A
JOB NO | 240 |  |  |  | QUANTITY | 22
| 1 | Tag No. | E-100(1)-LCS, E-100(2)-LCS, E-100(3)-LCS, E-100(4)-LCS,
E-300A(1)-LCS, E-300A(2)-LCS, E-300B(1)-LCS, E-300B(2)-LCS,
E-400A(1)-LCS, E-400A(2)-LCS, E-400B(1)-LCS, E-400B(2)-LCS,
P-800-LCS, CT-100-LCS, P-403-LCS, P-404-LCS, P-300A-LCS,
P-300B-LCS, P-301A-LCS, P-301B-LCS + 2 Nos. Spare
GENERAL | 2 | Quantity | 22
| 3 | Service | Cooler & Pump
| 4 | Location | Outdoor
ENCLOSURE SPECIFICATION | 5 | Material Box | GRP |  |  | Stainless Steel
|  |  | Aluminium Die Cast |  |  | Welded Steel Plate
| 6 | Protection Cover / Sun Shade | Yes |  | No
| 7 | Pedestal Stand | Yes |  | No
| 8 | Stand Height | 1 meter
ELECTRICAL | 9 | Voltage | 230 VAC |  | 110 VAC |  | 24VDC
| 10 | Current | 10 A
| 11 | Phase | Single |  | Three
| 12 | Frequency | 50 Hz
| 13 | Number of Push Button Switch | 2 (On & Off)
| 14 | Number of Indication | 2 (Red LED & Green LED)
| 15 | Selector Switch | 1(Local/Off/Remote)
| 16 | Terminal Block | 12 (with numbering 1~12)
| 17 | Ground Terminal Block | 1
PROTECTION | 18 | Protection Degree | IP 65
| 19 | Explosion Proof Mark | Exd IIB T4
OTHERS | 20 | Installation Type | Hang | Stand
| 21 | Dimension | VTA
| 22 | Weight | VTA
| 23 | Manufacturer | Reputed
2015-12-05
LCS with Selector Switch
BANGLADESH PETROLEUM EXPLORATION & PRODUCTION CO. LTD.
BANGLADESH PETROLEUM EXPLORATION & PRODUCTION CO. LTD.

## LCS without Selector Sw.
ELECTRICAL
DATA SHEET
USER | BANGLADESH PETROLEUM E&P CO. LTD. |  |  |  |  | DOC NO | 240-0301-EMEL-DS00-0002
LOCATION | SRIKAIL GAS FIELD,BANGLADESH |  |  |  |  | NAME | Local Control Station
PROJECT | 60 MMSCFD SILICAGEL DEHYDRATION TYPE GAS PROCESS PLANT |  |  |  |  | Version | A
JOB NO | 240 |  |  |  |  | QUANTITY | 6
| 1 | Tag No. |  | P-100A-LCS, P-100B-LCS, P-200A-LCS, P-200B-LCS +2 Nos. Spare
GENERAL | 2 | Quantity |  | 6
| 3 | Service |  | Cooler & Pump
| 4 | Location |  | Outdoor
ENCLOSURE SPECIFICATION | 5 | Material Box |  | GRP |  |  | Stainless Steel
|  |  |  | Aluminium Die Cast |  |  | Welded Steel Plate
| 6 | Protection Cover / Sun Shade |  | Yes |  | No
| 7 | Pedestal Stand |  | Yes |  | No
| 8 | Stand Height |  | 1 meter
ELECTRICAL | 9 | Voltage |  | 230 VAC |  | 110 VAC |  | 24VDC
| 10 | Current |  | 10 A
| 11 | Phase |  | Single |  | Three
| 12 | Frequency |  | 50 Hz
| 13 | Number of Push Button Switch |  | 2 (On & Off)
| 14 | Number of Indication |  | 2 (Red LED & Green LED)
| 15 | Selector Switch |  | N/A
| 16 | Terminal Block |  | 12 (with numbering 1~12)
| 17 | Ground Terminal Block |  | 1
PROTECTION | 18 | Protection Degree |  | IP 65
| 19 | Explosion Proof Mark |  | Exd IIB T4
OTHERS | 20 | Installation Type |  | Hang | Stand
| 21 | Dimension |  | VTA
| 22 | Weight |  | VTA
| 23 | Manufacturer |  | Reputed
|  | 2015-12-05 | 3
LCS without Selector Switch
BANGLADESH PETROLEUM EXPLORATION & PRODUCTION CO. LTD.
BANGLADESH PETROLEUM EXPLORATION & PRODUCTION CO. LTD.