## COVER
CONSORTIUM OF
SINOPEC PETROLEUM ENGINEERING CORPORATION.
AND
ZICOM EQUIPMENT PTE. LTD.
BANGLADESH PETROLEUM EXPLORATION & PRODUCTION CO. LTD.
[6 empty] | 29 Tuas Avenue 3 Singapore 639420 |  |  |  | Tel | : +65 6865 1765
[6 empty] | E-mail | : zepl@zicomgroup.com |  |  | Fax | : +65 6865 1764
ELECTRICAL CALCULATION SHEET
[8 empty] | Doc. No: | 240-0214-EMEL-CS00-0008
|  | Job No. |  | : | 240
|  | Client |  | : | BANGLADESH PETROLEUM EXPLORATION & PRODUCTION CO. LTD.
|  | Location |  | : | SRIKAIL GAS FIELD, BANGLADESH
|  | Item No. |  | : | -
|  | Description |  | : | FAULT LEVEL CALCULATION
|  | Project Title. |  | : | 60 MMSCFD GLYCOL DEHYDRATION TYPE GAS PROCESS PLANT
|  | Year Built |  | : | 2015
A | 2015-05-12 |  | 4 | ISSUED FOR APPROVAL | [5 empty] | AS | MH | VG
Rev. | Date |  | Page | Description of Revision | [5 empty] | Prepared | Checked | Approved
ZICOM

## AFC(Busbar Group B)
CONSORTIUM OF
| Electrical Calculation |  | ZICOM EQUIPMENT PTE LTD.
| Sheet |  | AND
SINOPEC PETROLEUM ENGINEERING CORPORATION
USER | BANGLADESH PETROLEUM EXPLORATION & PRODUCTION CO. LTD. |  |  |  | DOC NO | 240-0214-EMEL-CS00-0008
LOCATION | SRIKAIL GAS FIELD, BANGLADESH |  |  |  | SERVICE | FAULT LEVEL CALCULATION
PROJECT | 60 MMSCFD SILICA GEL DEHYDRATION TYPE NATURAL GAS PLANT |  |  |  | TAG NO
JOB NO | 240 |  |  |  | QUANTITY
Generator KVA Rating | 345 | kVA
Line to Line Voltage | 400 | V
Line to Neutral Voltage | 230 | V
Full Load Ampere | 497.98 | A
Genset Alternator Percentage Impedance | 12.5 | %
Fault at zero distance/terminal |  |  | Fault at zero distance/terminal
Full Load Ampreres | 498 | A | Full Load Ampreres |  | 498 | A
Multiplier,M1 | 8 |  | Multiplier,M1 |  | 8
Fault at Generator terminal | 3984 | A | Fault at Generator terminal |  | 5976 | A
L-L Fault | 3.98 | kA | L-N Fault |  | 5.98 | kA
L-L-L Fault(AFC) | 4.58 | kA
For BUSBAR GROUP B
Fault at some distance from terminal |  |  | Fault at some distance from terminal
Distance from terminal, L | 10 | ft | Distance from terminal, L |  | 10 | ft
No. of Conductor,N | 1 |  | No. of Conductor,N |  | 1
Conductor factor,C | 129900 |  | Conductor factor,C |  | 129900
Factor,f | 0.0013 |  | Factor,f |  | 0.004
Multiplier,M2 | 0.9987 |  | Multiplier,M2 |  | 0.996
Fault after 1st distance | 3979 | A | Fault after 1st distance |  | 5952.1 | A
L-L Fault | 3.98 | kA | L-N Fault |  | 5.95 | kA
L-L-L Fault(AFC) | 4.57 | kA
Note |  | Formula
Reff. Drawing: 240-0214-EMEL-DW00-0008 POWER |  | For L-L Fault |  | For L-N Fault
DISTRIBUTION SYSTEM
For conductor factor, C reff. document is attached |  | FLA L-L= |  | FLA L-N =
FLA=Full Load Ampere
AFC=Available Fault Current |  | Multiplier, M1 = |  | Multiplier, M2 =
L-L Fault=Approx. 87% L-L-L Fault
Sub-transient Reactance Per Unit,Xd''=0.125 |  | Factor, f = |  | Factor, f =
For low resistance Percent Impedance≈12.5%
Percent Reactance data is found from Generator |  | I(SCA)= Short Circuit Current at the beginning of the circuit
datasheet of Model No: PG345B3 |  | L=Length of Cable
N=No. of Conductor Per Phase
C=Conductor factor(One over the impedance per foot)
E(L-L)=Phase to Phase Voltage or L-L Voltage
E(L-N)=Phase to Neutral Voltage or L-N Voltage
ZICOM
BANGLADESH PETROLEUM EXPLORATION & PRODUCTION CO. LTD.

## AFC(Busbar Group C&D)
CONSORTIUM OF
| Electrical Calculation |  | ZICOM EQUIPMENT PTE LTD.
| Sheet |  | AND
SINOPEC PETROLEUM ENGINEERING CORPORATION
USER | BANGLADESH PETROLEUM EXPLORATION & PRODUCTION CO. LTD. |  |  |  | DOC NO | 240-0214-EMEL-CS00-0008
LOCATION | SRIKAIL GAS FIELD, BANGLADESH |  |  |  | SERVICE | FAULT LEVEL CALCULATION
PROJECT | 60 MMSCFD SILICA GEL DEHYDRATION TYPE NATURAL GAS PLANT |  |  |  | TAG NO
JOB NO | 240 |  |  |  | QUANTITY
Generator KVA Rating | 345 | kVA
Line to Line Voltage | 400 | V
Line to Neutral Voltage | 230 | V
Full Load Ampere | 497.98 | A
Genset Alternator Percentage Impedance | 12.5 | %
Fault at zero distance/terminal |  |  | Fault at zero distance/terminal
Full Load Ampreres | 498 | A | Full Load Ampreres |  | 498 | A
Multiplier,M1 | 8 |  | Multiplier,M1 |  | 8
Fault at Generator terminal | 3984 | A | Fault at Generator terminal |  | 5976 | A
L-L Fault | 3.98 | kA | L-N Fault |  | 5.98 | kA
L-L-L Fault(AFC) | 4.58 | kA
For BUSBAR GROUP C&D
Fault at some distance from terminal |  |  | Fault at some distance from terminal
Distance from terminal, L | 820 | ft | Distance from terminal, L |  | 820 | ft
No. of Conductor,N | 1 |  | No. of Conductor,N |  | 1
Conductor factor,C | 799 |  | Conductor factor,C |  | 799
Factor,f | 17.7041 |  | Factor,f |  | 53.331
Multiplier,M2 | 0.0535 |  | Multiplier,M2 |  | 0.0184
Fault after 1st distance | 214 | A | Fault after 1st distance |  | 109.96 | A
L-L Fault | 0.21 | kA | L-N Fault |  | 0.11 | kA
L-L-L Fault(AFC) | 0.25 | kA
Note |  | Formula
Reff. Drawing: 240-0214-EMEL-DW00-0008 POWER |  | For L-L Fault |  | For L-N Fault
DISTRIBUTION SYSTEM
For conductor factor, C reff. document is attached |  | FLA L-L= |  | FLA L-N =
FLA=Full Load Ampere
AFC=Available Fault Current |  | Multiplier, M1 = |  | Multiplier, M2 =
L-L Fault=Approx. 87% L-L-L Fault
Sub-transient Reactance Per Unit,Xd''=0.125 |  | Factor, f = |  | Factor, f =
For low resistance Percent Impedance≈12.5%
Percent Reactance data is found from Generator |  | I(SCA)= Short Circuit Current at the beginning of the circuit
datasheet of Model No: PG345B3 |  | L=Length of Cable
N=No. of Conductor Per Phase
C=Conductor factor(One over the impedance per foot)
E(L-L)=Phase to Phase Voltage or L-L Voltage
E(L-N)=Phase to Neutral Voltage or L-N Voltage
ZICOM
BANGLADESH PETROLEUM EXPLORATION & PRODUCTION CO. LTD.

## AFC(Busbar Group E)
CONSORTIUM OF
| Electrical Calculation |  | ZICOM EQUIPMENT PTE LTD.
| Sheet |  | AND
SINOPEC PETROLEUM ENGINEERING CORPORATION
USER | BANGLADESH PETROLEUM EXPLORATION & PRODUCTION CO. LTD. |  |  |  | DOC NO | 240-0214-EMEL-CS00-0008
LOCATION | SRIKAIL GAS FIELD, BANGLADESH |  |  |  | SERVICE | FAULT LEVEL CALCULATION
PROJECT | 60 MMSCFD SILICA GEL DEHYDRATION TYPE NATURAL GAS PLANT |  |  |  | TAG NO
JOB NO | 240 |  |  |  | QUANTITY
Generator KVA Rating | 345 | kVA
Line to Line Voltage | 400 | V
Line to Neutral Voltage | 230 | V
Full Load Ampere | 497.98 | A
Genset Alternator Percentage Impedance | 12.5 | %
Fault at zero distance/terminal |  |  | Fault at zero distance/terminal
Full Load Ampreres | 498 | A | Full Load Ampreres |  | 498 | A
Multiplier,M1 | 8 |  | Multiplier,M1 |  | 8
Fault at Generator terminal | 3984 | A | Fault at Generator terminal |  | 5976 | A
L-L Fault | 3.98 | kA | L-N Fault |  | 5.98 | kA
L-L-L Fault(AFC) | 4.58 | kA
For BUSBAR GROUP E
Fault at some distance from terminal |  |  | Fault at some distance from terminal
Distance from terminal, L | 20 | ft | Distance from terminal, L |  | 20 | ft
No. of Conductor,N | 1 |  | No. of Conductor,N |  | 1
Conductor factor,C | 981 |  | Conductor factor,C |  | 981
Factor,f | 0.3517 |  | Factor,f |  | 1.0594
Multiplier,M2 | 0.7398 |  | Multiplier,M2 |  | 0.4856
Fault after 1st distance | 2948 | A | Fault after 1st distance |  | 2901.95 | A
L-L Fault | 2.95 | kA | L-N Fault |  | 2.9 | kA
L-L-L Fault(AFC) | 3.39 | kA
Note |  | Formula
Reff. Drawing: 240-0214-EMEL-DW00-0008 POWER |  | For L-L Fault |  | For L-N Fault
DISTRIBUTION SYSTEM
For conductor factor, C reff. document is attached |  | FLA L-L= |  | FLA L-N =
FLA=Full Load Ampere
AFC=Available Fault Current |  | Multiplier, M1 = |  | Multiplier, M2 =
L-L Fault=Approx. 87% L-L-L Fault
Sub-transient Reactance Per Unit,Xd''=0.125 |  | Factor, f = |  | Factor, f =
For low resistance Percent Impedance≈12.5%
Percent Reactance data is found from Generator |  | I(SCA)= Short Circuit Current at the beginning of the circuit
datasheet of Model No: PG345B3 |  | L=Length of Cable
N=No. of Conductor Per Phase
C=Conductor factor(One over the impedance per foot)
E(L-L)=Phase to Phase Voltage or L-L Voltage
E(L-N)=Phase to Neutral Voltage or L-N Voltage
ZICOM
BANGLADESH PETROLEUM EXPLORATION & PRODUCTION CO. LTD.