## COVER
CONSORTIUM OF
SINOPEC PETROLEUM ENGINEERING CORPORATION.
AND
ZICOM EQUIPMENT PTE. LTD.
BANGLADESH PETROLEUM EXPLORATION & PRODUCTION CO. LTD.
[6 empty] | 29 Tuas Avenue 3 Singapore 639420 |  |  |  | Tel | : +65 6865 1765
[6 empty] | E-mail | : zepl@zicomgroup.com |  |  | Fax | : +65 6865 1764
POWER CABLE SCHEDULE
[8 empty] | Doc. No: | 240-0201-EMEL-CL00-0001
|  | Job No. |  | : | 240
|  | Client |  | : | BANGLADESH PETROLEUM EXPLORATION & PRODUCTION CO. LTD.
|  | Location |  | : | SRIKAIL GAS FIELD, BANGLADESH
|  | Item No. |  | : | -
|  | Description |  | : | POWER CABLE SCHEDULE
|  | Project Title. |  | : | 60 MMSCFD SILICA GEL DEHYDRATION TYPE GAS PROCESS PLANT
|  | Year Built |  | : | 2015
A | 28/10/2015 |  | 4 | ISSUED FOR APPROVAL | [5 empty] | AS | MH | VG
Rev. | Date |  | Page | Description of Revision | [5 empty] | Prepared | Checked | Approved
ZICOM

## Power Cable Schedule
Power Cable Schedule
USER |  |  | BANGLADESH PETROLEUM EXPLORATION & PRODUCTION CO. LTD. |  |  |  | DOC NO. : | 240-0201-EMEL-CL00-0001 |  |  |  | Rev : A
LOCATION |  |  | SRIKAIL GAS FIELD, BANGLADESH |  |  |  | SERVICE :
PROJECT |  |  | 60 MMSCFD SILICA GEL DEHYDRATION TYPE GAS PROCESS PLANT |  |  |  | TAG NO. : | N/A
JOB NO. |  |  | 240 |  |  |  | QUANTITY: | N/A
Sl.No | TAG NO. | DISCRIPTION |  |  | SOURCE | DESTINATION | CABLE SIZE (sqmm) | CABLE LENGTH (Meter) | CABLE VOLTAGE | Power Factor (p.f) | CABLE TYPE | CONDUCTOR | LOAD
1 | G-01 | GENERATOR 01 |  |  | G1 | MCC | 8 (1C X 150mm2) | 260 | 600V | 0.85 | PVC ARMOURED | COPPER | 276 KW
2 | G-02 | GENERATOR 02 |  |  | G2 | MCC | 8 (1C X 150mm2) | 300 | 600V | 0.85 | PVC ARMOURED | COPPER | 276 KW
3 | G-03 | GENERATOR 03 |  |  | G3 | MCC | 8 (1C X 150mm2) | 340 | 600V | 0.85 | PVC ARMOURED | COPPER | 276 KW
4 | GRID | NATIONAL GRID LINE |  |  | GRID LINE | MCC | 4C X 95mm2 |  | 600V | 0.85 | PVC ARMOURED | COPPER
5 |  | SPARE-1-25A |  |  |  |  | 4C X 10mm2 | 100 | 600V | 0.85 | PVC ARMOURED | COPPER | 14.7 KW
6 |  | SPARE-2-50A |  |  |  |  | 4C X 16mm2 | 100 | 600V | 0.85 | PVC ARMOURED | COPPER | 29.44 KW
7 |  | SPARE-3-50A |  |  |  |  | 4C X 16mm2 | 100 | 600V | 0.85 | PVC ARMOURED | COPPER | 29.44 KW
8 |  | SPARE-4-50A |  |  |  |  | 4C X 16mm2 | 100 | 600V | 0.85 | PVC ARMOURED | COPPER | 29.44 KW
9 |  | SPARE-5-50A |  |  |  |  | 4C X 16mm2 | 100 | 600V | 0.85 | PVC ARMOURED | COPPER | 29.44 KW
10 | C-501 | UTILITY AIR COMPRESSOR LOCAL CONTROL PANEL |  |  | MCC | C-501 | 4C X 10mm2 | 80 | 600V | 0.85 | PVC ARMOURED | COPPER | 15 KW
11 | C-502 | UTILITY AIR COMPRESSOR LOCAL CONTROL PANEL |  |  | MCC | C-502 | 4C X 10mm2 | 80 | 600V | 0.85 | PVC ARMOURED | COPPER | 15 KW
12 | C-503 | UTILITY AIR COMPRESSOR LOCAL CONTROL PANEL |  |  | MCC | C-503 | 4C X10mm2 | 80 | 600V | 0.85 | PVC ARMOURED | COPPER | 15 KW
13 |  | DOMESTIC & OFFICE USE |  |  | MCC | DOMESTIC & OFFICE USE | 4C X 35mm2 | 240 | 600V | 0.85 | PVC ARMOURED | COPPER | 50 KW
14 |  | GENERATOR & MCC ROOM DISTRIBUTION PANEL |  |  | MCC | GENERATOR & MCC ROOM DISTRIBUTION PANEL | 4C X 6mm2 | 40 | 600V | 0.85 | PVC ARMOURED | COPPER | 10 KW
15 | P-100A | CONDENSATE TRANSFER PUMP |  |  | MCC | P-100A | 4C X 4mm2 | 210 | 600V | 0.85 | PVC ARMOURED | COPPER | 5.5 KW
| P-100B | CONDENSATE TRANSFER PUMP |  |  | MCC | P-100B | 4C X 4mm2 | 210 | 600V | 0.85 | PVC ARMOURED | COPPER | 5.5KW
16 | P-100A-LCS | CONDENSATE TRANSFER PUMP-LCS |  |  | MCC | P-100A-LCS | 12C X 1.5mm2 | 210 | 600V | 0.85 | PVC ARMOURED | COPPER
| P-100B-LCS | CONDENSATE TRANSFER PUMP-LCS |  |  | MCC | P-100B-LCS | 12C X 1.5mm2 | 210 | 600V | 0.85 | PVC ARMOURED | COPPER
17 | P-200A | COOLING WATER PUMP |  |  | MCC | P-200A | 4C X 4mm2 | 160 | 600V | 0.85 | PVC ARMOURED | COPPER | 5.5 KW
| P-200B | COOLING WATER PUMP |  |  | MCC | P-200B | 4C X 4mm2 | 160 | 600V | 0.85 | PVC ARMOURED | COPPER | 5.5 KW
18 | P-200A-LCS | COOLING WATER PUMP-LCS |  |  | MCC | P-200A | 12C X 1.5mm2 | 160 | 600V | 0.85 | PVC ARMOURED | COPPER
| P-200B-LCS | COOLING WATER PUMP-LCS |  |  | MCC | P-200B | 12C X 1.5mm2 | 160 | 600V | 0.85 | PVC ARMOURED | COPPER
19 | E-100(1) | DRY AIR COOLER |  |  | MCC | E-100(1) | 4C X 16mm2 | 150 | 600V | 0.85 | PVC ARMOURED | COPPER | 22 KW
| E-100(1)-LCS | DRY AIR COOLER-LCS |  |  | MCC | E-100(1)-LCS | 12C X 1.5mm2 | 150 | 600V | 0.85 | PVC ARMOURED | COPPER
20 | E-100(2) | DRY AIR COOLER |  |  | MCC | E-100(2) | 4C X 16mm2 | 150 | 600V | 0.85 | PVC ARMOURED | COPPER | 22 KW
| E-100(2)-LCS | DRY AIR COOLER-LCS |  |  | MCC | E-100(2)-LCS | 12C X 1.5mm2 | 150 | 600V | 0.85 | PVC ARMOURED | COPPER
21 | E-100(3) | DRY AIR COOLER |  |  | MCC | E-100(3) | 4C X 10mm2 | 150 | 600V | 0.85 | PVC ARMOURED | COPPER | 15 KW
| E-100(3)-LCS | DRY AIR COOLER-LCS |  |  | MCC | E-100(3)-LCS | 12C X 1.5mm2 | 150 | 600V | 0.85 | PVC ARMOURED | COPPER
22 | E-100(4) | DRY AIR COOLER |  |  | MCC | E-100(4) | 4C X 10mm2 | 150 | 600V | 0.85 | PVC ARMOURED | COPPER | 15 KW
| E-100(4)-LCS | DRY AIR COOLER-LCS |  |  | MCC | E-100(4)-LCS | 12C X 1.5mm2 | 150 | 600V | 0.85 | PVC ARMOURED | COPPER
23 | E-300A(1) | REGENERATION GAS COOLER |  |  | MCC | E-300A(1) | 4C X 16mm2 | 165 | 600V | 0.85 | PVC ARMOURED | COPPER | 22 KW
| E-300A(1)-LCS | REGENERATION GAS COOLER-LCS |  |  | MCC | E-300A(1)-LCS | 12C X 1.5mm2 | 165 | 600V | 0.85 | PVC ARMOURED | COPPER
24 | E-300A(2) | REGENERATION GAS COOLER |  |  | MCC | E-300A(2) | 4C X 10mm2 | 165 | 600V | 0.85 | PVC ARMOURED | COPPER | 15 KW
| E-300A(2)-LCS | REGENERATION GAS COOLER-LCS |  |  | MCC | E-300A(2)-LCS | 12C X 1.5mm2 | 165 | 600V | 0.85 | PVC ARMOURED | COPPER
25 | E-300B(1) | REGENERATION GAS COOLER |  |  | MCC | E-300B(1) | 4C X 16mm2 | 165 | 600V | 0.85 | PVC ARMOURED | COPPER | 22 KW
| E-300B(1)-LCS | REGENERATION GAS COOLER-LCS |  |  | MCC | E-300B(1)-LCS | 12C X 1.5mm2 | 165 | 600V | 0.85 | PVC ARMOURED | COPPER
26 | E-300B(2) | REGENERATION GAS COOLER |  |  | MCC | E-300B(2) | 4C X 10mm2 | 165 | 600V | 0.85 | PVC ARMOURED | COPPER | 15 KW
| E-300B(2)-LCS | REGENERATION GAS COOLER-LCS |  |  | MCC | E-300B(2)-LCS | 12C X 1.5mm2 | 165 | 600V | 0.85 | PVC ARMOURED | COPPER
27 | E-400A(1) | COOLING GAS COOLER |  |  | MCC | E-400A(1) | 4C X 16mm2 | 165 | 600V | 0.85 | PVC ARMOURED | COPPER | 22 KW
| E-400A(1)-LCS | COOLING GAS COOLER-LCS |  |  | MCC | E-400A(1)-LCS | 12C X 1.5mm2 | 160 | 600V | 0.85 | PVC ARMOURED | COPPER
28 | E-400A(2) | COOLING GAS COOLER |  |  | MCC | E-400A(2) | 4C X 10mm2 | 160 | 600V | 0.85 | PVC ARMOURED | COPPER | 15 KW
| E-400A(2)-LCS | COOLING GAS COOLER-LCS |  |  | MCC | E-400A(2)-LCS | 12C X 1.5mm2 | 160 | 600V | 0.85 | PVC ARMOURED | COPPER
29 | E-400B(1) | COOLING GAS COOLER |  |  | MCC | E-400B(1) | 4C X 16mm2 | 160 | 600V | 0.85 | PVC ARMOURED | COPPER | 22 KW
| E-400B(1)-LCS | COOLING GAS COOLER-LCS |  |  | MCC | E-400B(1)-LCS | 12C X 1.5mm2 | 160 | 600V | 0.85 | PVC ARMOURED | COPPER
30 | E-400B(2) | COOLING GAS COOLER |  |  | MCC | E-400B(2) | 4C X 10mm2 | 160 | 600V | 0.85 | PVC ARMOURED | COPPER | 15 KW
| E-400B(2)-LCS | COOLING GAS COOLER-LCS |  |  | MCC | E-400B(2)-LCS | 12C X 1.5mm2 | 160 | 600V | 0.85 | PVC ARMOURED | COPPER
31 | P-800 | KOD PUMP |  |  | MCC | P-800 | 4C X 2.5mm2 | 180 | 600V | 0.85 | PVC ARMOURED | COPPER | 3 KW
| P-800-LCS | KOD PUMP-LCS |  |  | MCC | P-800-LCS | 12C X 1.5mm2 | 180 | 600V | 0.85 | PVC ARMOURED | COPPER
32 | CT-100 | WET COOLER |  |  | MCC | CT-100 | 4C X 6mm2 | 185 | 600V | 0.85 | PVC ARMOURED | COPPER | 11 KW
| CT-100-LCS | WET COOLER-LCS |  |  | MCC | CT-100-LCS | 12C X 1.5mm2 | 185 | 600V | 0.85 | PVC ARMOURED | COPPER
33 | V-502A/B | AIR DRYER |  |  | MCC | V-502A/B | 3C X 2.5mm2 | 80 | 600V | 0.85 | PVC ARMOURED | COPPER | 1 KW
34 | V-503A/B | AIR DRYER |  |  | MCC | V-503A/B | 3C X 2.5mm2 | 80 | 600V | 0.85 | PVC ARMOURED | COPPER | 1 KW
35 | LCP-0801 | FLARE STACK LOCAL CONTROL PANEL |  |  | MCC | FLARE STACK LOCAL CONTROL PANEL | 4CX 2.5mm2 | 180 | 600V | 0.85 | PVC ARMOURED | COPPER | 3 KW
|  | FLARE PANEL |  |  | CONTROL PANEL | FLARE PANEL | 3CX 2.5mm2 | 40 | 600V | 0.85 | PVC ARMOURED | COPPER
|  | BURN PIT PANEL |  |  | CONTROL PANEL | BURN PIT PANEL | 3CX 2.5mm2 | 40 | 600V | 0.85 | PVC ARMOURED | COPPER
36 | H-100 | WATER BATH HEATER |  |  | MCC | CONTROL BUILDING | 4CX 2.5mm2 | 240 | 600V | 0.85 | PVC ARMOURED | COPPER | 6 KW
37 | H-200 | REGENERATION GAS HEATER |  |  | MCC | CONTROL BUILDING | 4CX 2.5mm2 | 240 | 600V | 0.85 | PVC ARMOURED | COPPER | 6 KW
38 | P-403 | DEEP WELL PUMP |  |  | MCC | P-403 | 4C X 6mm2 | 310 | 600V | 0.85 | PVC ARMOURED | COPPER | 11 KW
| P-403-LCS | DEEP WELL PUMP -LCS |  |  | MCC | P-403-LCS | 12C X 1.5mm2 | 310 | 600V | 0.85 | PVC ARMOURED | COPPER
39 | P-404 | POTABLE WATER PUMP |  |  | MCC | P-404 | 4C X 2.5mm2 | 310 | 600V | 0.85 | PVC ARMOURED | COPPER | 0.75 KW
| P-404-LCS | POTABLE WATER PUMP-LCS |  |  | MCC | P-404-LCS | 12C X 1.5mm2 | 310 | 600V | 0.85 | PVC ARMOURED | COPPER
40 | P-401A | JOCKEY PUMP CONTROL PANEL |  |  | MCC | P-401A | 4C X 10mm2 | 280 | 600V | 0.85 | PVC ARMOURED | COPPER | 18 KW
41 | P- 401B | JOCKEY PUMP CONTROL PANEL |  |  | MCC | P-401B | 4C X 10mm2 | 280 | 600V | 0.85 | PVC ARMOURED | COPPER | 18 KW
42 | P-402A | DIESEL FIRE WATER PUMP CONTROL PANEL |  |  | MCC | P-402A | 4C X 2.5mm2 | 280 | 600V | 0.85 | PVC ARMOURED | COPPER | 3 KW
43 | P-402B | DIESEL FIRE WATER PUMP CONTROL PANEL |  |  | MCC | P-402B | 4C X 2.5mm2 | 280 | 600V | 0.85 | PVC ARMOURED | COPPER | 3 KW
44 | P-300A | CONDENSATE RECYCLE PUMP |  |  | MCC | P-300A | 4CX 2.5mm2 | 280 | 600V | 0.85 | PVC ARMOURED | COPPER | 0.75 KW
45 | P-300B | CONDENSATE RECYCLE PUMP |  |  | MCC | P-300B | 4CX 2.5mm2 | 280 | 600V | 0.85 | PVC ARMOURED | COPPER
46 | P-300A-LCS | CONDENSATE RECYCLE PUMP-LCS |  |  | MCC | P-300A-LCS | 12CX1.5mm2 | 280 | 600V | 0.85 | PVC ARMOURED | COPPER
47 | P-300B-LCS | CONDENSATE RECYCLE PUMP-LCS |  |  | MCC | P-300B-LCS | 12CX1.5mm2 | 280 | 600V | 0.85 | PVC ARMOURED | COPPER
48 | P-301A | TREATED WATER TRANSFER PUMP |  |  | MCC | P-301A | 4CX 2.5mm2 | 280 | 600V | 0.85 | PVC ARMOURED | COPPER | 0.75 KW
49 | P-301B | TREATED WATER TRANSFER PUMP |  |  | MCC | P-301B | 4CX 2.5mm2 | 280 | 600V | 0.85 | PVC ARMOURED | COPPER
50 | P-301A-LCS | TREATED WATER TRANSFER PUMP-LCS |  |  | MCC | P-301A-LCS | 12CX1.5mm2 | 280 | 600V | 0.85 | PVC ARMOURED | COPPER
51 | P-301B-LCS | TREATED WATER TRANSFER PUMP-LCS |  |  | MCC | P-301B-LCS | 12CX1.5mm2 | 280 | 600V | 0.85 | PVC ARMOURED | COPPER
52 | 02-GBC-1401 | GENERATOR BATTERY CHARGER |  |  | MCC | 02-GBC-1401 | 3CX 4mm2 | 30 | 600V | 0.85 | PVC ARMOURED | COPPER | 1.5 KW
53 | 02-UPS-1201 | UPS SYSTEM 1 |  |  | MCC | UPS-1 | 3CX 4mm2 | 240 | 600V | 0.85 | PVC ARMOURED | COPPER | 6 KVA
54 | 02-UPS-1202 | UPS SYSTEM 2 |  |  | MCC | UPS-2 | 3CX 4mm2 | 240 | 600V | 0.85 | PVC ARMOURED | COPPER | 6 KVA
55 | 02-UPS-1201 & 02-UPS-1202 | UPS-1&2-DB |  |  | UPS-1&2 | UPS-1&2-DB | 3CX 4mm2 | 10 | 600V | 0.85 | PVC ARMOURED | COPPER
|  | DCS PANEL |  |  | UPS-1&2 | DCS PANEL | 3CX 2.5mm2 | 70 | 600V | 0.85 | PVC ARMOURED | COPPER | 0.4 KW
|  | ENGINEERING STATION |  |  | UPS-1&2 | ENGINEERING STATION | 3CX 2.5mm2 | 50 | 600V | 0.85 | PVC ARMOURED | COPPER | 0.4 KW
|  | OPERATOR STATION 1 |  |  | UPS-1&2 | OPERATOR STATION | 3CX 2.5mm2 | 50 | 600V | 0.85 | PVC ARMOURED | COPPER | 0.4 KW
|  | OPERATOR STATION 2 |  |  | UPS-1&2 | OPERATOR STATION | 3CX 2.5mm2 | 50 | 600V | 0.85 | PVC ARMOURED | COPPER | 0.4 KW
|  | 75" MONITOR -1 |  |  | UPS-1&2 | 75" MONITOR -1 | 3CX 2.5mm2 | 50 | 600V | 0.85 | PVC ARMOURED | COPPER | 0.4 KW
|  | 75" MONITOR -2 |  |  | UPS-1&2 | 75" MONITOR -2 | 3CX 2.5mm2 | 50 | 600V | 0.85 | PVC ARMOURED | COPPER | 0.4 KW
|  | FIELD I/O ( RIO - 0001A) |  |  | UPS-1&2 | FIELD I/O ( RIO - 0001A) | 3CX 2.5mm2 | 80 | 600V | 0.85 | PVC ARMOURED | COPPER | 0.25 KW
|  | FIELD I/O ( RIO - 0001B) |  |  | UPS-1&2 | FIELD I/O ( RIO - 0001B) | 3CX 2.5mm2 | 80 | 600V | 0.85 | PVC ARMOURED | COPPER | 0.25 KW
|  | FIELD I/O ( RIO - 0001C) |  |  | UPS-1&2 | FIELD I/O ( RIO - 0001C) | 3CX 2.5mm2 | 80 | 600V | 0.85 | PVC ARMOURED | COPPER | 0.25 KW
|  | FIELD I/O ( RIO - 0002A) |  |  | UPS-1&2 | FIELD I/O ( RIO - 0002A) | 3CX 2.5mm2 | 80 | 600V | 0.85 | PVC ARMOURED | COPPER | 0.25 KW
|  | FIELD I/O ( RIO - 0002B) |  |  | UPS-1&2 | FIELD I/O ( RIO - 0002B) | 3CX 2.5mm2 | 230 | 600V | 0.85 | PVC ARMOURED | COPPER | 0.25 KW
|  | MCC I/O ( RIO - 0003) |  |  | UPS-1&2 | MCC I/O ( RIO - 0003) | 3CX 2.5mm2 | 250 | 600V | 0.85 | PVC ARMOURED | COPPER | 0.25 KW
|  | F&G UPS - 1KVA |  |  | UPS-1&2 | F&G UPS(UPS-3) | 3CX 2.5mm2 | 20 | 600V | 0.85 | PVC ARMOURED | COPPER | 1 KW
|  | PAGING & INTERCOM SYSTEM |  |  | UPS-1&2 | PAGING | 3CX 2.5mm2 | 30 | 600V | 0.85 | PVC ARMOURED | COPPER | 0.05 KW
|  | WATER BATH HEATER |  |  | UPS-1&2 | WATER BATH HEATER | 3CX 2.5mm2 | 40 | 600V | 0.85 | PVC ARMOURED | COPPER | 0.2 KW
|  | LCP ( REGENERATION GAS HEATER) |  |  | UPS-1&2 | LCP ( REGENERATION GAS HEATER) | 3CX 2.5mm2 | 40 | 600V | 0.85 | PVC ARMOURED | COPPER | 0.2 KW
|  | FLOW COMPUTER PANEL |  |  | UPS-1&2 | FLOW COMPUTER PANEL | 3CX 2.5mm2 | 50 | 600V | 0.85 | PVC ARMOURED | COPPER | 0.06 KW
|  | CCTV CAMERA |  |  | UPS-1&2 | CCTV CAMERA | 3CX 2.5mm2 | 350 | 600V | 0.85 | PVC ARMOURED | COPPER | 0.1 KW
|  | CCTV CAMERA |  |  | UPS-1&2 | CCTV CAMERA | 3CX 2.5mm2 | 350 | 600V | 0.85 | PVC ARMOURED | COPPER | 0.1 KW
|  | CCTV CAMERA |  |  | UPS-1&2 | CCTV CAMERA | 3CX 2.5mm2 | 50 | 600V | 0.85 | PVC ARMOURED | COPPER | 0.1 KW
|  | DVR NETWORKABLE |  |  | UPS-1&2 | DVR NETWORKABLE | 3CX 2.5mm2 | 50 | 600V | 0.85 | PVC ARMOURED | COPPER | 0.08 KW
|  | PRINTER 1 & 2 |  |  | UPS-1&2 | PRINTER | 3CX 2.5mm2 | 50 | 600V | 0.85 | PVC ARMOURED | COPPER | 0.15 KW
|  | FIRE & GAS SYSTEM |  |  | 3CX 2.5mm2 | UPS-1&2-DB | FIRE & GAS SYSTEM | 30 | 600V | 0.85 | PVC ARMOURED | COPPER | 0.25 KW
|  | FLARE CONTROL PANEL |  |  | UPS-1&2-DB | FLARE CONTROL PANEL | 3CX 2.5mm2 | 330 | 600V | 0.85 | PVC ARMOURED | COPPER | 0.04 KW
|  | POWER CABLE FOR GC |  |  | UPS | GC | 3CX 2.5mm2 | 140 | 600V | 0.85 | PVC ARMOURED | COPPER | 0.05 KW
|  | UPS-3 |  |  | UPS-1&2-DB | UPS-3 | 3CX 2.5mm2 | 20 | 600V | 0.85 | PVC ARMOURED | COPPER | 1 KW
|  | UPS-3-DB |  |  | UPS-3 | UPS-3-DB | 3CX 2.5mm2 | 10 | 600V | 1.85 | PVC ARMOURED | COPPER | 0.1 KW
56 | 02-UPS-1203 | FIRE PANEL |  |  | UPS-3-DB | FIRE PANEL | 3CX 2.5mm2 | 40 | 600V | 0.85 | PVC ARMOURED | COPPER | 0.05 KW
|  | FIRE MIMIC PANEL |  |  | UPS-3-DB | FIRE MIMIC PANEL | 3CX 2.5mm2 | 20 | 600V | 0.85 | PVC ARMOURED | COPPER | 200W
|  | ALARM SYSTEM |  |  | UPS-3-DB | ALARM SYSTEM | 3CX 2.5mm2 | 20 | 600V | 0.85 | PVC ARMOURED | COPPER | 140W
|  | POWER SUPPLY |  |  | UPS-3-DB | POWER SUPPLY | 3CX 2.5mm2 | 10 | 600V | 0.85 | PVC ARMOURED | COPPER | 18 KW
57 | LDP-1401 | LIGHTING DISTRIBUTION PANEL |  |  | MCC | LIGHT PANEL | 5C X 10mm2 | 20 | 600V | 0.85 | PVC ARMOURED | COPPER | 18 KW
|  | TELECSCOPIC TOWER -1 |  |  | LIGHT PANEL | TELECSCOPIC TOWER -1 | 3C X 2.5mm2 | 130 | 600V | 0.85 | PVC ARMOURED | COPPER | 1.2 KW
|  | TELECSCOPIC TOWER -2 |  |  | LIGHT PANEL | TELECSCOPIC TOWER -2 | 3C X 2.5mm2 | 180 | 600V | 0.85 | PVC ARMOURED | COPPER | 1.2 KW
|  | TELECSCOPIC TOWER -3 |  |  | LIGHT PANEL | TELECSCOPIC TOWER -3 | 3C X 2.5mm2 | 200 | 600V | 0.85 | PVC ARMOURED | COPPER | 1.2 KW
|  | PIPE RACK LIGHT-1 |  |  | LIGHT PANEL | PIPE RACK LIGHT-1 | 3C X 2.5mm2 | 160 | 600V | 0.85 | PVC ARMOURED | COPPER | 0.7 KW
|  | PIPE RACK LIGHT-2 |  |  | LIGHT PANEL | PIPE RACK LIGHT-2 | 3C X 2.5mm2 | 170 | 600V | 0.85 | PVC ARMOURED | COPPER | 0.5 KW
|  | STREET LIGHT -1 |  |  | LIGHT PANEL | STREET LIGHT -1 | 3C X 2.5mm2 | 150 | 600V | 0.85 | PVC ARMOURED | COPPER | 0.45 KW
|  | STREET LIGHT -2 |  |  | LIGHT PANEL | STREET LIGHT -2 | 3C X 2.5mm2 | 70 | 600V | 0.85 | PVC ARMOURED | COPPER | 0.45 KW
|  | INSTRUMENT AIR AREA SHED LIGHT |  |  | LIGHT PANEL | INSTRUMENT AIR AREA SHED LIGHT | 3C X 2.5mm2 | 80 | 600V | 0.85 | PVC ARMOURED | COPPER | 0.036 KW
|  | TRANSFER PUMP SHED LIGHT |  |  | LIGHT PANEL | TRANSFER PUMP SHED LIGHT | 3C X 2.5mm2 | 250 | 600V | 0.85 | PVC ARMOURED | COPPER | 0.036 KW
|  | DELUGE VALVE SHED LIGHT |  |  | LIGHT PANEL | DELUGE VALVE SHED LIGHT | 3C X 2.5mm2 | 330 | 600V | 0.85 | PVC ARMOURED | COPPER | 0.036 KW
|  | FIRE WATER SHED LIGHT |  |  | LIGHT PANEL | FIRE WATER SHED LIGHT | 3C X 2.5mm2 | 330 | 600V | 0.85 | PVC ARMOURED | COPPER | 0.036 KW
|  | LOADING ARM SHED LIGHT |  |  | LIGHT PANEL | LOADING ARM SHED LIGHT | 3C X 2.5mm2 | 200 | 600V | 0.85 | PVC ARMOURED | COPPER | 0.4 KW
|  | AIR CRAFT WARNING LIGHT |  |  | LIGHT PANEL | AIR CRAFT WARNING LIGHT | 3C X 2.5mm2 | 300 | 600V | 0.85 | PVC ARMOURED | COPPER | 0.05 KW
A | 28/10/2015 |  |  | ISSUED FOR APPROVAL | [6 empty] | AS | MH | VG
REV | DATE |  |  | DESCRIPTION OF REVISION | [6 empty] | PREPARED | CHECKED | APPROVED
ZICOM
CONSORTIUM OF
SINOPEC PETROLEUM ENGINEERING CORPORATION
AND
ZICOM EQUIPMENT PTE. LTD.
BANGLADESH PETROLEUM EXPLORATION & PRODUCTION CO. LTD.